SNAKE SPRING TOWNSHIP MUNICIPAL AUTHORITY

SEWER OPERATING RULES AND REGULATIONS

Updated and Effective January 1, 2023

SECTION 2   DEFINITIONS

2.01   Unless the context specifically indicates otherwise, the meaning of the terms used shall be as follows:

A.  Application:  Form upon which a prospective user signifies their desire for sewer service.

B.  Authority:  The Snake Spring Township Municipal Authority and its duly authorized representatives and employees.

C.  Building:  Each single family dwelling unit, multiple dwelling unit, multiple use unit, store, shop, office, business, institutional, commercial, or industrial unit contained within any structure, erected and intending for continuous or periodic habitation, occupancy or use by human beings or animals and from which structure sewage or wastes are or may be discharged, located in the Township.

D.  Building Conduits:  Pipes installed by the owner to convey sewage or wastes from source to a point of connection.

E.  Commonwealth:  Commonwealth of Pennsylvania.

F.  Connection:  That part of the sewer system extending from the end of the service line to the plumbing fixtures in the building.

G.  Capacity Fee:  An initial, one time assessment for all future customers -- and initial and future multi-users (more than one equivalent dwelling unit) --to assist in paying for the construction of the wastewater treatment plant or the future expansion of said plant.**

H.  Developer:  Any person who desires to construct, at their own cost and expense, a sewer system extension to serve any one or more buildings and to connect the sewer system extension to the sewer system.

**Definition "G" was amended on August 2, 1993.

I.  EDU (Equivalent Dwelling Unit):  The number of gallons determined by the Authority as the average number of gallons of sewage disposed of per day by an average dwelling.  The EDU rate effective July 1, 2006 shall be 150 gallons.**

J.  Engineer:  A registered professional engineer retained by the Authority, including any authorized member of the staff of such engineer.

K.  Inspector:  The person or persons appointed by the Authority to inspect the sewer system (including both public, semi-public, and private sewer systems), service lines, connections, and all other connections between building conduits and sewer mains.

L.  Large Consumer:  Consumer who consistently uses more than 20,000 gallons of water per month.

M.  May: Is permissive.

N.  Meter:  The part of the water system which registers and records the consumption of water.

O.  Multiple Dwelling Unit:  Apartments, multi-family or multi-unit, and multi-family dwelling projects.  Does not include motels or  hotels.

P.  Multiple Use Unit:  A combination of a single family dwelling unit, store, shop, office, business, institutional, commercial or industrial unit contained within any structure or any building determined by the Authority to have more than one use.

Q.  Owner:  Any person vested with ownership, legal or equitable, sole or partial, of real estate served by the sewer system.

R.  Person:  An individual, firm, company, association, society, corporation, or other group or entity.

S.  Pressure Sewer:  A sewer line transporting wastewater, flowing full and pressurized by mechanical surcharge or by virtue of negative grade.

T.  Service Line (Authority’s Sewer Line):  That part of the sewer system including the wye, saddle, and pipe extending from the sewer main to the property line (connection).***

U.  Sewer Main:  A pipe or conduit that carries sanitary sewage and other wastes.

** Definition "I" was amended on May 1, 1995 and then amended on July 1, 2006.

***Definition “T” was amended on August 3, 2009.

V.  Sewer System:  The pipe, manholes, fittings and appurtenances owned and operated by the Authority, including any additions thereto or extensions thereof, in furnishing sewer service.

W.  Shall:  Is mandatory.

X.  Tap Fee:  An initial, one-time assessment to cover the cost of the physical installation of the sewage collection system, its amortization, and is intended to be in accordance with House Bill 444 (Act 1990-203).  Please note that this fee does not include the surcharge for expanded capacity of treatment facilities, which will be covered by the "Capacity Fee" for new customer hookups.**

Y.  Tenant:  Any building occupant other than the owner who utilizes the services of the sewer system.

Z.  Township:  Township of Snake Spring, Bedford County, Pennsylvania.

AA.  User:  The party, either owner or tenant who is an agent or representative of the owner, contracting with the Authority for sewer service for one or more families or business institutional unit on one property owned or tenanted by the party or parties.

AB. Variable Grade Sewer:  A sewer line transporting only septic tank effluent which is constructed independent of grade and having a net positive drop in total elevation.

AC. Other Terms:  Unless the context specifically indicates otherwise, the meaning of terms not defined above shall be as defined in the "Glossary-Water and Wastewater Control Engineering", prepared by joint editorial board representing:  American Public Health Association, American Society of Civil Engineers, American Water Works Association and Water Pollution Control Federation.

AD. Line Extension: An addition to the Authority’s main line which is necessary to serve the premises of a customer.***

AE.  Residential Service: Water service supplied to an individual single-family residential dwelling unit or to Multiple Dwelling Units and to Multiple Use Units.***

** Section 2.01 X was amended August 2, 1993.

***Section 2.01 AD and AE were amended August 3, 2009.

SECTION 3   PROHIBITION OF SEPTIC TANKS, CESSPOOLS, AND PRIVY VAULTS

3.01   It shall be unlawful for any owner of property within the Township who is required to connect to the Sewer System to employ any means, either by septic tank, cesspool, privy vault, or other depository for the disposal of acceptable sewage other than into and through the said sewer system.  No connection, to any public sanitary sewer, will be allowed from any septic tank, cesspool, privy vault, or other depository, with the special exception where pressure sewers or variable grade sewers exist as the sewer main.

In either case, the old septic tank may or may not be discontinued depending on the inspection of said tank by the Authority's inspector.  If needed, a new septic tank (which will be provided to the owner by the Authority) will be installed by the owner as part of his connection.  The earlier mentioned depositories, at the time of making of connection of the building to the sewer system, shall be abandoned and filled with select fill in all other cases.  The Authority, at its cost, will supply new septic tank(s) and pump pits with pumps, if necessary, provided a building was connected during 1992-1993 as part of the original Authority System.   In all other cases the owner will provide, at their cost, the Authority approved septic tank(s) and pump pits with pumps if necessary.**

** Section 3.01 was amended April 3, 1995.

SECTION 4   REQUIRED CONNECTION

4.01   Each owner of any building within the Township,  located on any property abutting any street, alley or right-of-way in which a sewer main has been provided  and where any part of building is within one hundred fifty (150) feet of said sewer right-of-way or sewer line, at his/her own expense shall connect his/her building to the sewer system in accordance with the Rules and  Regulations within ninety (90) days after the date of official written notice from the Authority to do so, unless otherwise refused a permit to connect by the Authority.***

4.01A   The actual building and connection to the sewer system must be made within one (1) year of the payment of the charges and fees required by the Authority’s Operating Rules and Regulations.  If properly requested by the property owner prior to the actual connections being made to the sewer main, the Authority will refund the required fees and charges less an administrative fee as set forth in the current Schedule of Fees and Charges.  After one (1) year, a new application must be made with appropriate fees and charges paid to the Authority.***

***Section 4.01 was amended August 3, 2009.

***Section 4.01A was added August 3, 2009 and on December 12, 2022.

SECTION 5   FAILURE TO CONNECT, DISCONNECT, OR MAKE REPAIRS, ALTERATIONS OR CHANGES AS REQUIRED BY THE AUTHORITY

5.01  In the event any owner of any building in the Township shall refuse or neglect to connect, disconnect, or make other repairs or changes as required within a ninety (90) day period, he shall be deemed to be in violation of the Rules and Regulations, and the Authority or its agents may enter upon the property to perform or cause to be performed such work and labor or cause to be furnished such material as may be necessary to complete the work.  An exception to the previous ninety (90) day notice period shall however occur when the owner of any building or structure is found to have broken or damaged cleanouts on the sewer lateral line serving said property.  The owner will have ten (10) days from date of written notice by the Authority to repair the cleanouts identified as needing repair.  The property owner shall notify the Authority when such cleanout repairs are completed.  If the property owner fails to repair the identified cleanouts within the ten (10) day notification period, the Authority or its agents may enter upon the property to perform or cause to be performed such work and labor or cause to be furnish such material as may be necessary to complete the work.  In such case, the Authority shall, upon completion of the work, send an itemized bill of the actual costs incurred therefore, together with a percentage addition thereof and all charges and expenses thereto (as set forth in the current Schedule of Fees and Charges).  In case of neglect or refusal by owner to pay the bill within thirty (30) days, it shall be the duty of the Authority to file municipal liens and take other collection action.  No owner of a building shall be required to connect a building to sewer system if the Authority determines that available sewer system capacity is insufficient to serve said building.**

** Section 5.01 was amended May 18, 1998, on May 2, 2005, on August 3, 2009, and on December 12, 2022.

SECTION 6   CONDITIONS AND PROCEDURES FOR INITIAL SERVICE

6.01   No person shall make or cause to be made any connection with the sewer system until they have fulfilled all the following conditions and procedures:

A.  Any person desiring the introduction of a service line and/or connection from the Authority's sewer system to service their building must first make a written application for a permit on a form furnished by the Authority, at least two (2) weeks before the service is required, stating the address location, the name of user, the purpose of use and character of structure for which the service will be used, and the size of the service line and connection desired.  No work of any nature shall commence before the issuance of the aforementioned permit.  Commercial, industrial, institutional, housing, subdivisions and other multi-users will likely require the filing of planning modules for land development. Filing of planning modules may require several months for approval.

B.  The application must be signed by the owner of the building or his duly authorized agent.  The application together with the Rules and Regulations of the Authority shall regulate and control the provision of sewer service to the building.

C.  The application must be accompanied by a required non-refundable application fee as set forth in the current Schedule of Fees and Charges.  The application will normally be acted upon at the next meeting after submitted to the Authority. If approved the applicant must forward the fees required herein to the Authority by the date specified or the application will be voided.  The excavator’s name and phone number also must be provided along with a current copy of their liability insurance. **

D.  The application for connection permit must contain indication of the date when the connection will be ready for inspection and the Building service line will be constructed.  Due to weather conditions, connections are generally made only between March 15 and November 15.***

E.  If approved for service the applicant will receive a signed copy of his Application for service as a record of his approved service.  **

** Section 6.01 (E) was amended on April 3, 1995.

** Section 6.01 (C) was amended on April 3, 1995, on August 3, 2009, and on December 12, 2022.

***Section 6.01 (D) was amended on August 3, 2009

6.02   When an application has been made for a new service or for reinstatement of or change in an existing service, it is assumed that all plumbing, piping and fixtures which will be serviced are in order to receive the service; and the Authority shall not be liable in any case for any accident, backup, break, or leakage arising in any way in connection with the acceptance of sewage flow or failure to accept sewage flow, or the freezing of pipes or fixtures, nor for any damage to the building from the usage or non-usage of sewer service provided to the building.

6.03   Each Applicant for new service shall place into escrow with the Authority a refundable deposit (as set forth in the current Schedule of Fees and Charges) upon Applicant requesting the Authority inspect its sewer connection.  At the time of application, the Applicant shall estimate the time usage of the connection will commence.  The escrow will be refunded when notice of move in and of usage is given to the Authority, provided notice is received prior to the estimated commencement date.  If the Authority has not received notice the usage has commenced by the estimated date, the Authority shall send out its inspector to determine the status of usage.  If, upon inspection, usage has commenced, the deposit shall be forfeited to the Authority and regular billing will commence.  If service has not commenced, another estimated usage date shall be provided by Applicant and the process repeated, provided, however, the Applicant shall pay an additional inspection fee as set forth in the current Schedule of Fees and Charges.  The Authority reserves the right to pursue any and all balances for usage by the Applicant prior to Applicant providing notice to the Authority or for the period prior to the Authority learning of Applicant’s use.**

In addition to the above, the Applicant shall notify the Authority office at least 48 hours prior to the time when inspection of a connection is requested, to allow for scheduling of an Authority inspector.  The inspector must be present to inspect and approve this construction.**

6.04   At any time of inspection of the connection, the owner shall permit the inspector full and complete access to all pipes and appurtenances, sanitary and drainage facilities, in each building and in and about all parts of the property.  No portion of the connection shall be covered over, or in any manner concealed, until after it is inspected and approved by the inspector.

6.05   No connection shall be laid in the same trench with a water or gas pipe within any facility of a public service company or within three (3) feet of any excavation without permission of the Authority.**

6.06   All new wells for water must be at least 50 feet from the nearest sewer line or manhole.  If it is not possible to place a well at least 50 feet from a sewer line or manhole, then the Authority shall authorize the installation of a well within 50 feet provided the well owner agrees to release and hold the Authority

harmless from any claim relative to the contamination of their well.  The release and hold harmless agreement will be prepared by the Authority's solicitor.**

6.07   Authority may require the owner to hydrostatically, pneumatically, dye or smoke test the connection, at the discretion of, and in a manner determined by the Authority.  In no case shall infiltration/exfiltration exceed one hundred (100) gallons per day per inch diameter per mile of pipe.

6.08   The inspector shall signify his approval of the connection by endorsing his name and date of approval on the aforementioned permit.

6.09   No "two party" (two (2) people sharing one (1) line) sewers will be allowed unless the opportunity exists that such sewer can further serve future development.  Any "two party" sewers shall meet all requirements stipulated in other sections of these Rules and Regulations.  Two (2) adjacent connections may  be allowed in the same trench along a common property line, at the discretion of the Authority and its engineer.**

** Section 6.03 was amended on April 3, 1995.

** Section 6.03 was amended on March 5, 2001 and on December 12, 2022.

** Section 6.05 was amended on April 6, 1992.

** Section 6.06 was added on August 2, 1993.

** Section 6.09 was amended on April 6, 1992.

SECTION 7   RIGHT TO INSPECTION

7.01   The Authority and its duly authorized representatives and employees, bearing proper credentials and identification, shall be permitted to enter upon all property for the purpose of inspection, observation, testing and re-testing the connection and all other matters pertaining to the discharge of wastes to the sewer system to ensure compliance with the Rules and Regulations, at all reasonable hours.

7.02  The inspection fee is per connection as set forth in the current Schedule of Fees and Charges.  The inspection fee is per visit by the inspector, with one visit being the norm unless the connection is found to be faulty.  The subsequent inspection will also cost the fee per connection as set forth in the current Schedule of Fees and Charges.  The inspection fee must be paid in advance to the Authority.  At the time of inspection of the building connection, and prior thereto in accordance with applicable easements, the Owner shall permit the Inspector full and complete access to all pipes and other appurtenances in each Building and about all parts of the property.  No portion of the Building Service Line shall be covered over, or in any manner concealed, until after it is satisfactorily inspected and approved by Inspector by a written notation on the connection permit.  The Inspector shall signify his approval of the Building Service by endorsing his name and the date of approval on the connection permit.**

** Section 7.02 was amended April 3, 1995, August 3, 2009, and December 12, 2022.

SECTION 8   SPECIFICATIONS AND STANDARDS

8.01   A separate connection shall be required for each building whether constructed as a detached unit or as one of a pair or row.  A single connection may be permitted to serve a school, factory or other permanent multiple dwelling unit or multiple use unit structure whose individual units may not be subject to separate ownership, at the discretion of the Authority.

8.02   No repairs, alterations or additions to any connections   shall be made unless the person desiring to make some shall first make application to and receive permission from the Authority.

8.03   No user shall be allowed to permit any other persons or buildings to use or connect with his connection except upon written permission of the Authority.

8.04   The minimum size connection for any building shall be four (4) inch diameter pipe laid on a minimum grade of one-fourth (1/4) inch per foot length, and having permanently sealed watertight and gas tight joints.  Smaller diameter pipes may be allowed in the case of pressure sewers and variable grade sewers, at the direction of the engineer.  The size of the connection serving other than detached residential units shall be considered on an individual basis by the Authority.

8.05   Service lines and/or connections shall not be installed when the connection passes through property which at the time may be the property of persons other than the owner of the building to be served, unless the owner of the building to be served obtains a right-of-way from the person whose property the connection will pass through.  The right-of-way shall be recorded with the Recorder of Deeds at the Bedford County Courthouse.  The connections of the service line to the connection  shall be placed at the limit of right-of-way abutting the sewer main.  The owner of the building to be served shall be responsible for the maintenance of the connection.  No other person may connect to the connection.

8.06   When an owner desires sewer service to a building which does not have any existing sewer main of adequate capacity in the roadway abutting the building, the owner shall be required to extend the sewer main at his sole cost.  Size of the sewer main and length that sewer main will have to be extended shall be determined by the engineer. Said extension shall require the written permission of the Authority, and, if appropriate, the proper Commonwealth permits obtained in the name of the  Authority at the sole cost of the owner.

8.07   All connection pipe shall be placed with at least six (6) inches of natural ground or tamped earth between pipe and any boulder or rock strata.  All connection pipe shall have at least thirty (30) inches of cover, mechanically tamped in layers not to exceed twelve (12) inches.  All connection pipe will be laid in a straight grade, avoiding summits and depressions.  Under driveways connection pipe shall be SDR 26 PVC placed on a six (6) inch 2RC aggregate base and backfilled with 2RC aggregate to at least twelve (12) inches above top of pipe.  Where rock is encountered on a trench bottom, over excavate six (6) inches and backfill with 2RC aggregate.  Minimum gravity pipe grade shall be two (2%) percent.  Variable grade sewer or pressure sewer connection may require a centrifugal pump after the septic tank, or an ejector (or grinder) pump just prior to the septic tank immediately followed by a back water prevention valve and/or a gate valve, as the engineer directs.

8.08   All connections to a new sewer main shall utilize a polyvinyl-chloride (PVC) wye conforming to ASTM D3034 or equal. All connections to an existing sewer main shall utilize a PVC hard coupler conforming to ASTM D3034.*

8.09   All service lines and connections shall be type SDR 35 PVC pipe conforming to ASTM D3034 or equal.

8.10   Within five (5) feet of any building or construction there shall be a double "B" trap, with a vent stack to the surface, one (1) foot above the finish grade.  The trap is to be constructed in such a manner so as to have access to the sanitary sewer through the stack toward the main line sewer.

If any residence or building is engaged in any food processing activity, fast food franchise, as a restaurant or in an operation that generates fatty grease waste product that congeals to a solid or semi-solid, the applicant must provide for a suitable grease trap ahead (upstream) of the double "B" trap that will effectively remove such waste product.  The grease trap must be pumped at the owners' expense at a time interval to be established to the satisfaction of the Authority.**

Any customer required by the Authority to utilize a grease trap must post a weekly record of trap inspection(s) and cleaning by employees.  Authority personnel will review the record when visited to ensure compliance.***

8.11   In areas where there will be variable grade sewers, it may be required that the owner install a new septic tank and possibly a pump, back water prevention valve and a gate valve as part of his making connection to the sewer main.  These items will be furnished by the Authority to the owner at no cost. In every case the septic tank will be inspected periodically, and pumped out as needed, at no cost to the owner. Location of the septic tank will be left to the  discretion  of  the  engineer  so  that  said tank is readily accessible to a sanitary hauling truck.  An easement of ten (10) feet in and around the septic tank and pump is implied here to give access for inspection, maintenance and pumping.  An easement of six (6) feet in and around the pump well is implied here to give access for inspection and maintenance.

8.12   A cleanout shall be provided by the applicant at any severe bend in the connection line, at the direction of the Authority's inspector or engineer.  In addition, a cleanout shall be provided by the applicant adjacent to the right-of-way line of the sewer main.****

* Section 8.08 was amended August 3, 2009.

**Section 8.10 was amended April 6, 1992.

***Section 8.10 was amended April 3, 1995.

****Section 8.12 was amended at unspecified date.

SECTION 9   CONSTRUCTION OF SYSTEM BY DEVELOPER

9.01   Any developer shall comply with the provisions of this Section.

9.02   A request for service for buildings where sewer main would be below an elevation which would require pumping facilities as determined by the engineer, which would be an additional operation and maintenance cost for the Authority will be discouraged.

9.03  The developer shall submit three (3) copies of plans for the proposed extension of the sewer system to the engineer for review, comments, recommendations and approval on 24" x 36" sheets showing plan view to a scale of 1" = 50' and profiles to a scale of 1" = 5' vertically and 1" = 50' horizontally, or such other scale as the engineer shall deem acceptable, a north point, a suitable title block, date and the name of the developers' engineer and imprint of his registration seal. The developer shall be responsible for reimbursing the Authority for any Engineering Review fees of the plans incurred as a result of the proposed extension.***

9.04   Prior to final acceptance of any sewer system extension by the Authority, the developer shall furnish to the Authority "Record Drawings" showing the location of all sewer mains, manholes, and service connections relative to permanent landmarks such as buildings, trees, utility poles or property

corners; the angle and distance between manholes, the top and invert elevation of each manhole, and the location of all service connections relative to the nearest manhole both upstream and downstream.

9.05   Easements for sewer mains and service lines constructed outside of dedicated street rights-of-way shall be recorded in the name of the Authority.

9.06   All pipe used for sewer main extensions shall be type SDR 35 PVC pipe conforming to ASTM D 3034 or equal.  The minimum size pipe for sewer main extensions shall be six (6) inch diameter, except where pressure sewers or variable grade sewers are proposed and approved.

9.07   Construction of sewer systems extensions will not be permitted until proper Commonwealth permits have been obtained in the name of the Authority by the developer.

9.08   All sewer main pipe shall be placed on a four (4) inch 2RC aggregate base and backfilled with 2RC aggregate base or an equivalent aggregate base approved by the Authority, to at least six (6) inches above top of pipe (or with select material to at least twelve (12) inches above top of pipe).  Where rock is encountered on the trench bottom over excavate six (6) inches and backfill with 2RC aggregate or an approved equivalent.  All pipe shall have at least forty-eight (48) inches of cover mechanically tamped in layers not to exceed twelve (12) inches.  Where pipe is installed in traveled portions of roadways, including shoulders, berms, median strips, etc., the pipe shall be backfilled with 2RC aggregate or an approved equivalent to the surface.**

***Section 9.03 was amended August 3, 2009

**Section 9.08 was amended in 2002.

9.09   All fittings shall be PVC conforming to ASTM D 3034 or equal.

9.10   Manholes shall be precast reinforced concrete manholes conforming to ASTM C-478.  Manhole opening shall be thirty (30) inch diameter.  Inside diameter of manhole shall be forty-eight (48) inch standard.  The manhole shall have a custom preform opening in manhole base to accommodate sewer pipe at time of manufacture.

9.11   Manhole frame shall be Allegheny Foundry Company Pattern No. 109 or equal.  Manhole frame shall have a twenty-seven (27) inch diameter opening.  Manhole cover shall be Allegheny Foundry Company  Pattern No. 110 or equal.  Material shall be cast iron, conforming to ASTM A-48, class 30.  The words "SANITARY SEWER" shall be embossed on cover.  The inside of all manholes, pump station holding tanks, manhole cover lids and any corrodible material exposed to sewer gasses and effluent must be coated with a protective agent such as a tar-based paint or other durable paint.

9.12   Manhole steps shall be of polypropylene plastic or extruded aluminum cast in manhole.

9.13   Flexible gasket type sealant shall be placed between all manhole sections, eccentric cone section and grade ring (if required) or manhole frame, and grade ring (if required) and manhole frame.  Flexible gasket-type sealant shall be RUB' R-NEK butyl rubber sealant, or equal, and shall conform to Federal Specification SS-S 210A.  Sealant shall be one (1) inch size.  Use two (2) sealant strips between manhole sections.

9.14   Manhole frame shall be fastened to eccentric can section of manhole with two (2) three-quarter (3/4) inch high strength low alloy steel all threads. A three-quarter (3/4) inch lead corker shall be used with each all thread.  All threads shall penetrate any and all grade rings used and manhole frame.

9.15   Ready mixed cement concrete for flow lines shall be 3,300 psi. equivalent to Pennsylvania Department of Transportation Class A cement concrete.

9.16   All sewer mains shall be subject to an air pressure test specified by engineer, such that infiltration/exfiltration shall not exceed 100 gallons per inch of pipe diameter per mile of pipe  per  day.  Developer shall provide air compressor, portable air control equipment, and all necessary apparatus for testing.  The duration of test shall be determined by the Authority’s inspection representative.

9.17   Depending on layout of existing sewer collection system and/or potential for future development beyond the area in question, the size of a sewer main extension could vary, based upon engineer review and recommendations.

9.18   Service lines shall be installed while sewer main extension is being constructed.

9.19   The developer or his contractor, at the Developer's cost, will make the connection of the sewer main extension to the sewer system.  The developer shall furnish the necessary fittings, and/or manhole to make the connection.  The actual connection shall be done in the presence of the Authority inspector. **

** Section 9.19 was amended April 3, 1995.

9.20   The sewer mains and all appurtenances shall be subject to full time inspection by the Authority's representative at the sole cost of the developer.  If the installation of the sewer mains or appurtenances has been properly made, written approval will be furnished to the developer or his designated representative. If the work is not satisfactory, the inspector shall advise what must be done to meet the Authority requirements.

9.21  No sewer main extension constructed by a developer will be approved for use and acceptance by the Authority until the sewer main is formally approved by the Authority, all connection and inspection fees have been paid, the Authority has been reimbursed in full for all inspections costs incurred by the inspector during construction, testing and approval, and the sewer main extension has been dedicated to the Authority.  The Developer shall be responsible for all necessary repairs to the extension for a one-year period from the date of formal approval by the Authority.***

*** Section 9.21 was amended August 3, 2009.

SECTION 10   MAINTENANCE AND REPAIR

10.01 The Authority shall have the ultimate responsibility for the use, operation, maintenance and repair of the sewer system from the terminal point of the interceptors up to and including the point of connection, but in no such event shall the Authority bear any responsibility beginning at the owner’s property line.  The owner of any building connected to the sewer system shall notify the Authority of any condition on his property which threatens the proper operation and integrity of the sewer system.***

10.02  All connections to the sewer system are the responsibility of the owner beginning at the owner’s property line and shall be maintained and repaired by the owner at his own cost with the exception of the following two (2) conditions:

A.  The septic tank (where variable grade sewer main is concerned) will be pumped by the Authority at an interval of time, from three (3) to six (6) years or as needed.

B.  The centrifugal pump or ejector pump will be maintained at no cost to the owner, in the case where the sewer main is pressure sewer.  Pump maintenance applies only to initial system customers where the Authority supplied the pump.**

The repairs to the connection shall be subject to the direction, approval, and inspection of the Authority.***

10.03   The Authority reserves the sole right to excavate or allow excavation of any sewer system component.  The Authority reserves the right to enter the property of the owner adjacent to the septic tank or pump well for the purpose of inspection or to pump out said tank, in cases where the sewer main is variable grade sewer or pressure sewer.

10.04   The Authority shall in no event be responsible for maintenance or damage done by sewage escaping from the connection or any other pipe fixture on the inlet side of the point of connection.

10.05   The owner shall keep the connection from the service line to the building in good condition at all times under penalty of discontinuance of service by the Authority, upon forty-eight (48) hours' notice. However, should a serious break or other accident occur on the owner's property which would threaten the Authority's sewer system or its capacity, the Authority reserves the right to discontinue service without notice until such time as the condition is corrected.

10.06   In the case of leakage, either into, or out of the sewers, the location of which is not readily apparent, the Authority will upon request of the user excavate in and about the point of connection for the purpose of determining the responsibility for the leak.  The Authority shall assume the costs of work if it is found that the leak is located between the point of connection and sewer main.  If the leak is determined to be between the point of connection and the building, the owner shall reimburse the Authority for the actual costs of the work required to determine responsibility.

10.07   The Authority may at any time require user to install in connection with his service pipes, such vents, traps, gates, or other apparatus as may be in the opinion of the Authority required for the safeguarding and protection of the Authority's or owner's property.

10.08   When it is necessary to renew an existing service line due to malfunction, the owner will renew the service line at its cost with the same size and the same location as the old service line.  Such work will require 48 hour advance notification to the Authority and inspection by and Authority inspector.**

10.09   When the owner desires a change in location or size of an existing service line, the cost of the change shall be borne entirely by the owner.

*** Section 10.01 was amended August 3, 2009.

** Section 10.02(B) was amended April 3, 1995.

***Section 10.02 was amended August 3, 2009.

** Section 10.08 was amended April 3, 1995.

SECTION 11   UNLAWFUL USE OF SEWER SYSTEM

11.01   No person connected to a service line of the Authority's sewer system shall discharge or cause to be discharged into the sewer system any storm water, surface  drainage, ground drainage, roof runoff, subsurface drainage, cooling water, spring water, or foundation drainage, or connect or cause to be connected to the sewer system in any way within or without the building any pipe, tile, or other conduit which has the capacity or purpose of conveying such waters.

11.02   No person shall connect, cause to be connected, or allow any other person to connect to the sewer system any building or other source of water or waste other than that for which the permit is or has been issued.

11.03   No person shall connect, cause to be connected, or allow any other person to connect, in any way to the sewer system any septic tank, cesspool, privy vault, or other depository of sewage or wastes, or cause or allow any discharge from any of said depositories to the sewer system, unless otherwise approved in writing by the  Authority.

11.04   No person shall make, or cause to be made, any cross connection between any pipe, fixture, or other appurtenance connected in any way to the sewer system and any public or private component of any potable water system or source whereby, in the opinion of the Authority, the potential exists for vacuums or back siphonage which could permit sanitary wastes to enter a potable water system or source.

SECTION 12    PROHIBITED WASTES

12.01   The discharge of excessive amounts of unpolluted water or waste to the sewer system is expressly prohibited.  The Authority reserves the right to define the amount it deems excessive in each particular instance.

12.02   The discharge of household garbage to the sewer system is expressly prohibited unless such garbage is first properly shredded.

12.03   The discharge of sewage or wastes to the sewer system from any property or building, other than for which a permit has been issued in accordance with these Rules and Regulations, is expressly prohibited.

12.04   The discharge of any wastes containing ashes, cinders, sand, mud, straw, shavings, metal, glass, rags, feathers, tar, plastics, wood, hair, chemical or paint residues, greases, paunch manure, lime slurry, or viscose material of such character or in such quantity that, in the opinion of the Authority, they may cause an obstruction to the flow in the sewers or otherwise interfere with the proper operation of the sewer system and any treatment facilities serving the sewer system shall be prohibited.

12.05   The discharge of any gasoline, benzine, naphtha, fuel oil, or other inflammable or explosive liquids, solids or gases, or any liquids, solids, or gases which by reason of their nature or quality may be in any way injurious to persons, property, or the equipment or structures of the sewer system or its operation, is prohibited.

12.06   The discharge of wastes containing any noxious, toxic, or malodorous gas or substance which either singly or interaction with sewage or other wastes may, in the opinion of the Authority, create a public nuisance or hazard to life or property, or prevent entry to sewer system structures for maintenance and repair, is prohibited.

12.07   The discharge of wastes containing toxic radioactive isotopes is prohibited without written permission of the Authority.

12.08   The discharge of any wastes not previously mentioned which are prohibited by the Pennsylvania Department of Environmental Resources, or prohibited by the Ordinances or Rules and Regulations of the Township of Snake Spring, Bedford County, or their respective authorities, by type, character or concentration, is prohibited.

12.09   Wastes having a temperature in excess of 150 degrees F. or less than 32 degrees F.

12.10   Wastes having PH lower than 5.5 or higher than 9.0 or having any corrosive property capable of causing damage or hazards to structures, equipment, or personnel of the sanitary sewer system.  Where the Township deems it advisable, it may require any person discharging industrial wastes  to install and maintain, at his own expense, in a manner approved by the Township,  a suitable device to continuously measure and record the PH of the wastes so discharged.

12.11   		Substance			Maximum Permissible Concentration

Phenolic compounds as C6H50H       			     0.0 mg/1

Cyanides as CN                     			     0.0 mg/1

Cyanates as CNO                   				1.0 mg/1

Iron as  Fe                  					1.5 mg/1

Trivalent Chromium as Cr      				       1.0 mg/1

Hexavalent Chromium as Cr  				       0.5 mg/1

Nickel as Ni                       				1.0 mg/1

Copper as Cu                       				1.0 mg/1

Lead as Pb                         				0.1 mg/1

Tin as SN                          				1.0 mg/1

Zinc  as Zn                        				0.1 mg/1

Calcium as Cd                      				0.1 mg/1

Mercury                            				0.05 mg/1

BOD							              300 mg/1

Suspended Solids                   				300 mg/1

Chloride                           				180 mg/1

Concentrations above these levels are prohibited.**

12.12   Wastes containing more than 30 mg/1 by weight of fat, oil or grease.

12.13   Wastes containing more than 10 mg/1 of any of the following gases:  hydrogen sulfide, sulfur dioxide, nitrous oxide, or any of the halogens.

12.14   Wastes containing gases or vapors, either free or occluded, in concentrations toxic or dangerous to humans or animals.

12.15   Any waste containing toxic substances in quantities sufficient to interfere with the biochemical processes of sewage treatment works or that will pass through the sewage treatment works and exceed the state or interstate requirements for the receiving stream.

12.16   Any expense or laboratory fees associated with testing for the presence of prohibited substances in a customer's raw sewage shall be borne by the customer if it is found that a customer's sewage contains impermissible concentrations of prohibited substances.**

** Section 12.11 was amended April 3, 1995.

** Section 12.16 was amended April 3, 1995.

SECTION 13  PRETREATMENT OF WASTEWATER*

*This section was adopted on August 8, 2022.

13.01 	Pretreatment Facilities

Users shall provide wastewater treatment as necessary to comply with these Rules and Regulations and shall achieve compliance with all categorical Pretreatment Standards, Local Limits, and the prohibitions set out in Section 12 of these Rules and Regulations within the time limitations specified by the State, or Authority, whichever is more stringent. Any facilities necessary for compliance shall be provided, operated, and maintained at the User’s expense.  Detailed plans describing such facilities and operating procedures shall be submitted to the Authority for review, and shall be acceptable to the Authority before such facilities are constructed.  The review of such plans and operating procedures shall in no way relieve the User from the responsibility of modifying such facilities as necessary to produce a discharge acceptable to the Authority under the provisions of these Rules and Regulations.

13.02 	Additional Pretreatment Measures

- Whenever deemed necessary, the Authority may require Users to restrict their discharge during peak flow periods, designate that certain wastewater be discharged only into specific sewer, relocate and/or consolidate points of discharge, separate sewage waste streams from industrial waste streams, and such other conditions as may be necessary to protect the Wastewater System and determine the User’s compliance with the requirements of these regulations.

- The Authority may require any person discharging into the Wastewater System to install and maintain, on their own property and at their expense, a suitable storage and flow-control facility to ensure equalization of flow. An individual wastewater discharge permit may be issued solely for flow equalization.

- Grease, oil, and sand interceptors shall be provided when, in the opinion of the Authority, they are necessary for the proper handling of wastewater containing excessive amounts of grease and oil, or sand; except that such interceptors shall not be required for residential users.  All interception units shall be of a type and capacity approved by the Authority.  Interceptor units shall be so located to be easily accessible for cleaning and inspection.  Such interceptors shall be inspected, cleaned, and repaired by the User at their expense.

- Users with the potential to discharge flammable substances may be required to install and maintain an approved combustible gas detection meter.

13.03 	Change in Operations

- Any industrial user contemplating or planning a substantial change in the manufacturing process, raw materials, auxiliary processes, pretreatment processes or other changes which may result in substantial changes to wastewater character, composition, volume or rate of flow, shall notify the Authority in writing at least thirty (30) days prior to making such a change, or, if the change is not planned thirty (30) days or more in advance, immediately upon the decision to make such a change. If a change in wastewater characteristics occurs without the knowledge of the industrial user, the industrial user shall report the change immediately upon becoming aware of it. The report shall include all information necessary to determine the effect on the wastewater from the change. The Authority may require the industrial user to undertake a compatibility study to demonstrate to the satisfaction of the Authority that the wastewater to be discharged is compatible with the sewer system, will not affect any requirements imposed upon the Authority (including sludge disposal requirements) and will not otherwise adversely affect the Wastewater System.

- The Authority may, on receipt of such a report:

  - Continue an existing wastewater discharge permit in effect.

  - Require application for a new wastewater discharge permit.

  - Modify an existing wastewater discharge permit to reflect the changed nature of the waste.

  - Rescind and reissue an existing wastewater discharge permit in order to make substantial changes in wastewater discharge permit conditions.

  - Revoke an existing wastewater discharge permit or require the industrial user to cease or prevent the discharge.

  - Take such other action as it deems appropriate.

13.04 	Slug Loads and Spills

Each industrial user shall provide protection from spills or accidental discharges that may result in unauthorized discharges or slug load discharges. Facilities to prevent spills and slug loads shall be provided and maintained at the owner or industrial user’s own cost and expense.

- NOTIFICATION:

In the case of a spill or slug load or other unauthorized discharge, it is the responsibility of the industrial user to, immediately upon discovery of the spill, slug load or other unauthorized discharge, telephone or notify the Authority of the waste (concentration and volume), corrective actions being taken or planned and expected duration.

- NOTICE TO EMPLOYEES:

A notice shall be permanently posted on the industrial user’s bulletin board or other prominent place advising employees whom to call in the event of a spill or other unauthorized discharge. Employers shall insure that all employees who may cause or suffer such a discharge to occur are advised of the emergency notification procedure.

- WRITTEN NOTICE:

Within five (5) days following a spill, slug load or other unauthorized discharge, the industrial user shall submit to the Authority a detailed written report describing the cause of the discharge and the measures to be taken by the industrial user to prevent similar future occurrences. Such notification shall not relieve the industrial user of any expense, loss, damage or other liability which may be incurred as a result of damage to the sewer system, fish kills or any other damage to person or property; nor shall such notification relieve the industrial user of any fines, civil penalties, other liability or applicable law. This notice requirement may be waived by the Authority for an industrial user which is not required to submit a plan under subsection (D), below.

- SPILL PREVENTION CONTROL AND COUNTERMEASURE (SPCC) PLAN:

  - All significant industrial users existing at the time of the enactment of these regulations shall complete and submit for approval a SPCC Plan or provide acceptable evidence that such a plan is not necessary for their facility, within nine (9) months of the enactment of these regulations.

  - No significant industrial user who commences discharge to the sewer system after the effective date of these regulations shall be permitted to introduce pollutants into the sewer system until it has completed and submitted for approval an SPCC plan or provided acceptable evidence that such a plan is not necessary for their facility. The Authority, at its discretion, may require an SPCC Plan for any other industrial user.

  - SPCC plans for significant industrial users shall, at a minimum, contain the following elements:

    - Description of discharge practices, including nonroutine batch discharges;

    - Description of stored chemicals;

    - Procedures for immediately notifying the Authority of any accidental or Slug Discharge, as required by this ordinance; and

    - Procedures to prevent adverse impact from any accidental or Slug Discharge.  Such procedures include, but are not limited to, inspection and maintenance of storage areas, handling and transfer of materials, loading and unloading operations, control of plant site runoff, worker training, building of containment structures or equipment, measures for containing toxic organic pollutants, including solvents, and/or measures and equipment for emergency response.

  - SPCC plans shall be submitted to the Authority for review and shall be approved by the Authority before implementation of the plan or construction of any required facilities. Review and approval of such plans, facilities and operating procedures by the Authority shall not relieve the industrial user from the responsibility to modify its facility as necessary to meet the requirements of the industrial pretreatment program, nor shall such a review and approval be deemed to constitute any assurance or warrant on the part of the Authority as to the effectiveness or safety of the SPCC plan.

13.05 	Requirement for Wastewater Discharge Permits

- All industrial dischargers shall file with the Authority, a complete wastewater discharge permit application.  The application shall contain wastewater information on the nature, characteristics or any other aspect deemed necessary by the Authority for determination of compliance with these Rules and Regulations, NPDES permit conditions, and state and federal law.

  - The Authority reserves the right to require periodic updates to the wastewater information.

  - Information requested and designated by the discharger as confidential is subject to the conditions of confidentiality – SEE SECTION 13.23.

  - The Authority reserves the right, at its sole discretion, to deny the issuance of a wastewater discharge permit, or to issue such a permit conditionally.

- Where a User owns, operates, or occupies properties designated as an industrial discharger at more than one location, separate information shall be required for each location as may be required by the Authority.

- The Authority may require other Users to obtain wastewater discharge permits as necessary to carry out the purposes of these regulations.

- Discharge of any industrial waste to the Wastewater System without a wastewater discharge permit or any violation of the terms and conditions of a wastewater discharge permit shall be deemed an unauthorized discharge subject to the penalties provided herein.

- Obtaining a wastewater discharge permit does not relieve a permittee of its obligation to comply with all Federal and State Pretreatment Standards or Requirements or with any other requirements of Federal, State, and local law.

  - Wastewater Discharge Permitting: Existing Conditions

- Any User required to obtain a wastewater discharge permit who was discharging wastewater into the Wastewater System prior to the effective date of these Rules and Regulations and who wishes to continue such discharges in the future, shall, within forty-five (45) days after said date, apply to the Authority for a wastewater discharge permit in accordance with Section 13.08 of these regulations, and shall not cause or allow discharges to the Wastewater System to continue after ninety (90) days of the effective date of these regulations unless a wastewater discharge permit has been issued by the Authority.

13.07 	Wastewater Discharge Permitting: New Connections

- Any User required to obtain a wastewater discharge permit who proposes to begin or recommence discharging into the Wastewater System must obtain such permit prior to the beginning or recommencing of such discharge.  An application for this wastewater discharge permit, in accordance with Section 13.08 of these regulations, must be filed at least ninety (90) days prior to the date upon which any discharge will begin or recommence.

13.08 	Wastewater Discharge Permitting: Permit Application Contents

- All Users required to obtain a wastewater discharge permit must submit a permit application along with an application fee as set forth in the current Schedule of Fees and Charges. The Authority may require Users to submit all or some of the following information as part of a permit application:

- Identifying Information.

  - The name and address of the facility, including the name of the operator and owner.

  - Contact information, description of activities, facilities, and plant production processes on the premises;

- Environmental Permits.

  - A list of any environmental control permits held by or for the facility.

- Description of Operations.

- A brief description of the nature, average rate of production (including each product produced by type, amount, processes, and rate of production), and standard industrial classifications of the operation(s) carried out by such User.  This description should include a schematic process diagram, which indicates points of discharge to the Wastewater System from the regulated processes.

- Types of wastes generated, and a list of all raw materials and chemicals used or stored at the facility which are, or could accidentally or intentionally be, discharged to the Wastewater System;

- Number and type of employees, hours of operation, and proposed or actual hours of operation;

- Type and amount of raw materials processed (average and maximum per day);

- Site plans, floor plans, mechanical and plumbing plans, and details to show all sewers, floor drains, and appurtenances by size, location, and elevation, and all points of discharge;

- Time and duration of discharges;

- The location for monitoring all wastes covered by the permit;

- Flow Measurement.  Information showing the measured average daily and maximum daily flow, in gallons per day, to the Wastewater System from regulated process streams and other streams, as necessary, to allow use of the combined waste stream formula set out in 40 CFR 403.6(e).

- Measurement of Pollutants.

  - The categorical Pretreatment Standards applicable to each regulated process and any new categorically regulated processes for Existing Sources.

  - The results of sampling and analysis identifying the nature and concentration, and/or mass, where required by the Standard or by the Authority of regulated pollutants in the discharge from each regulated process.

  - Instantaneous, Daily Maximum, and long-term average concentrations, or mass, where required, shall be reported.

  - The sample shall be representative of daily operations and shall be analyzed in accordance with procedures set out in Section 13.20 of these Rules and Regulations.  Where the Standard requires compliance with a BMP or pollution prevention alternative, the User shall submit documentation as required by the Authority or the applicable Standards to determine compliance with the Standard.

  - Sampling must be performed in accordance with procedures set out in Section 13.20 of these regulations.

- Any other information as may be deemed necessary by the Authority to evaluate the permit application.

- Incomplete or inaccurate applications will not be processed and will be returned to the User for revision.

13.09 	Application Signatories and Certifications

- All wastewater discharge permit applications, User reports and certification statements must be signed by an Authorized Representative of the User and contain the certification statement in Section 13.25.

- If the designation of an Authorized Representative is no longer accurate because a different individual or position has responsibility for the overall operation of the facility or overall responsibility for environmental matters for the company, a new written authorization satisfying the requirements of this Section must be submitted to the Authority prior to or together with any reports to be signed by an Authorized Representative.

13.10 	Wastewater Discharge Permit Decisions

- The Authority will evaluate the data furnished by the User and may require additional information.  Within forty-five (45) days of receipt of a complete permit application, the Authority will determine whether to issue a wastewater discharge permit.  The Authority may deny any application for a wastewater discharge permit.

13.11 	Wastewater Discharge Permit Issuance

- WASTEWATER DISCHARGE PERMIT DURATION

A wastewater discharge permit shall be issued for a specified time period, not to exceed five (5) years from the effective date of the permit.  A wastewater discharge permit may be issued for a period less than five (5) years, at the discretion of the Authority.  Each wastewater discharge permit will indicate a specific date upon which it will expire. The industrial user shall apply for reissuance of the wastewater discharge permit a minimum of ninety (90) days prior to the expiration of the industrial user’s existing wastewater discharge permit.

- WASTEWATER DISCHARGE PERMIT CONTENTS

A wastewater discharge permit shall include such conditions as are deemed reasonably necessary by the Authority to prevent Pass Through or Interference, protect the quality of the water body receiving the treatment plant’s effluent, protect worker health and safety, facilitate sludge management and disposal, and protect against damage to the Wastewater System.

  - Wastewater discharge permits must contain:

    - A statement that indicates the wastewater discharge permit issuance date, expiration date and effective date;

    - A statement that the wastewater discharge permit is nontransferable without prior notification to the Authority in accordance with Section 13.13 of these regulations, and provisions for furnishing the new owner or operator with a copy of the existing wastewater discharge permit;

    - Effluent limits, including Best Management Practices, based on applicable Pretreatment Standards;

    - Self-monitoring, sampling, reporting, notification, and record-keeping requirements.  These requirements shall include an identification of pollutants (or best management practice) to be monitored, sampling location, sampling frequency, and sample type based on Federal, State, and local law.

    - A statement of applicable civil and criminal penalties for violation of Pretreatment Standards and Requirements, and any applicable compliance schedule.  Such schedule may not extend the time for compliance beyond that required by applicable Federal, State, or local law.

    - Requirements to control Slug Discharge, if determined by the Authority to be necessary.

  - Individual wastewater discharge permits may contain, but need not be limited to, the following conditions:

- Limits on the average and/or maximum rate of discharge, time of discharge, and/or requirements for flow regulation and equalization;

- Requirements for the installation of pretreatment technology, pollution control, or construction of appropriate containment devices, designed to reduce, eliminate, or prevent the introduction of pollutants into the treatment works;

- Requirements for the development and implementation of spill control plans or other special conditions including management practices necessary to adequately prevent accidental, unanticipated, or nonroutine discharges;

- Development and implementation of waste minimization plans to reduce the amount of pollutants discharged to the Wastewater System;

- The unit charge or schedule of User charges and fees for the management of the wastewater discharged to the Wastewater System;

- Requirements for installation and maintenance of inspection and sampling facilities and equipment, including flow measurement devices;

- A statement that compliance with the wastewater discharge permit does not relieve the permittee of responsibility for compliance with all applicable Federal and State Pretreatment Standards, including those which become effective during the term of the individual wastewater discharge permit; and

- Other conditions as deemed appropriate by the Authority to ensure compliance with these Rules and Regulations, and State and Federal laws, rules, and regulations.

13.12 	Modifications of Wastewater Discharge Permits

- The Authority may modify an individual wastewater discharge permit for good cause, including, but not limited to, the following reasons:

  - To incorporate any new or revised Federal, State, or local Pretreatment Standards or Requirements;

  - To address significant alterations or additions to the User’s operation, processes, or wastewater volume or character since the time of the individual wastewater discharge permit issuance;

  - A change in the Wastewater System that requires either a temporary or permanent reduction or elimination of the authorized discharge;

  - Information indicating that the permitted discharge poses a threat to the Authority’s Wastewater System, Authority personnel, or the receiving waters;

  - Violation of any terms or conditions of the wastewater discharge permit;

  - Misrepresentations or failure to fully disclose all relevant facts in the wastewater discharge permit application or in any required reporting;

  - Revision of or a grant of variance from categorical Pretreatment Standards pursuant to 40 CFR 403.13;

  - To correct typographical or other errors in the individual wastewater discharge permit; or

  - To reflect a transfer of the facility ownership or operation to a new owner or operator where requested in accordance with Section 13.13.

13.13 	Transfer of Wastewater Discharge Permits

Wastewater discharge permits may be transferred to a new owner or operator only if the permittee gives at least ninety (90) days advance notice to the Authority and the Authority approves the transfer of the wastewater discharge permit.  The notice to the Authority must include a written certification by the new owner or operator which:

- States that the new owner and/or operator has no immediate intent to change the facility’s operations and processes;

- Identifies the specific date on which the transfer is to occur; and

- Acknowledges full responsibility for complying with the existing individual wastewater discharge permit.

13.14 	Revocation of Wastewater Discharge Permits

The Authority may revoke a wastewater discharge permit for good cause, including, but not limited to, the following reasons:

- Failure to notify the Authority of significant changes to the  wastewater prior to the changed discharge;

- Failure to provide prior notification to the Authority of changed conditions pursuant to Section 12 of these Rules and Regulations;

- Misrepresentation or failure to fully disclose all relevant facts in the wastewater discharge permit application;

- Falsifying selfmonitoring reports and certification statements;

- Tampering with monitoring equipment;

- Refusing to allow the Authority timely access to the facility premises and records;

- Failure to meet effluent limitations;

- Failure to pay fines or failure to pay permitting or application fees;

- Failure to pay sewer charges;

- Failure to meet compliance schedules;

- Failure to complete a wastewater survey or the wastewater discharge permit application;

- Failure to provide advance notice of the transfer of business ownership of a permitted facility; or

- Violation of any Pretreatment Standard or Requirement, or any terms of the wastewater discharge permit or these regulations.

Wastewater discharge permits shall be voidable upon cessation of operations or transfer of business ownership.  All wastewater discharge permits issued to a User are void upon the issuance of a new individual wastewater discharge permit to that User.

13.15 	Reissuance of Wastewater Discharge Permits

A User with an expiring wastewater discharge permit shall apply for wastewater discharge permit reissuance by submitting a complete permit application, in accordance with Section 13.08 of these regulations, a minimum of ninety (90) days prior to the expiration of the User’s existing wastewater discharge permit.

If a User has applied for reissuance in accordance with this Section, and the wastewater discharge permit is not renewed on or before the expiration date through no fault of the User, then the existing wastewater discharge permit shall remain in effect pending a decision on the application for reissuance by the Authority.

13.16 	Baseline Monitoring Reports

- Where an industrial user, subject to a newly promulgated categorical pretreatment standard (i.e., an existing source), has not previously submitted an application for a wastewater discharge permit, as required by Section 13.08 of these regulations, the industrial user shall, within one hundred eighty (180) days after the promulgation of the applicable categorical standard:

  - Apply for a wastewater discharge permit.

  - Provide the baseline monitoring information required by 40 CFR §403.12 (b) (this information may be incorporated into the application for a wastewater discharge permit).

  - Provide a compliance schedule for meeting the pretreatment standards as required by 40 CFR §403.12 (c) if such a schedule is required.

- An industrial user with an existing wastewater discharge permit shall submit to the Authority within one hundred eighty (180) days after the promulgation of an applicable categorical standard the information required by 40 CFR §403.12 (b).

- A new source or industrial user that become a categorical industrial user through a change in facilities or processes, shall submit a report containing the information required by 40 CFR §403.12 (b) at least ninety (90) days prior to commencement of discharge from the regulated process or facility. This information may be incorporated into the application for a wastewater discharge permit submitted in such time frame.

- Baseline monitoring reports shall be signed and certified by an authorized representative in accordance with Section 13.25 and 40 CFR §403.12 (I).

13.17 	Categorical Compliance Reports

Within ninety (90) days following the date for final compliance with applicable categorical standards or, in the case of a new source, following the commencement of the discharge of industrial waste from processes regulated by categorical standards into the sewer system, any industrial user subject to categorical standards shall submit to the Authority a report in accordance with 40 CFR §403.12 (d), including information indicating the nature and concentration of all pollutants in the discharge from the regulated process which are limited by categorical standards and the average and maximum daily flows for those process units in the industrial user’s facility which are limited by such categorical standards. The report shall certify that the information contained therein concerning wastewater constituents and flows is representative of discharges during normal work cycles. The report shall also state whether the applicable categorical standards are being met on a consistent basis and, if not, what additional operation and management practices and/or pretreatment is necessary to bring the industrial user into compliance with the applicable categorical standards, and including a schedule for completion of the required actions in the form described in 40 CFR §403.12 (b)(7). Such a schedule shall not have a compliance date later than that established for the applicable categorical standard. This statement shall be signed by an authorized representative of the industrial user in accordance with Section 13.25 and 40 CFR §403.12 (1) and 403.6 (a) (2) (ii), and certified by a certified professional.

13.18 	Periodic Compliance Reports

- All significant industrial users shall report to the Authority on form prescribed by the Authority, at least twice a year; the date of the report to be determined by the Authority. Reports may be required more frequently as deemed necessary by the Authority.

- The report required under the section shall contain the information required by 40 CFR §403.12 (e), 403.12 (g) and/or 403.12 (h), as applicable including, at a minimum, the measured concentrations of all pollutants regulated by categorical standards or otherwise regulated by wastewater discharge permit, a record of any measured daily flows and a statement of accuracy and completeness signed and certified by the authorized representative of the significant industrial user in accordance with 40 CFR §403.12 (1) and 403.6 (a) (2) (ii). Reports shall also contain any other information as required by the Authority.

- For significant industrial users subject to categorical standards, if discharge limits are based on mass units per production unit, then production information regarding the regulated processes during the reporting period shall be included in the report, along with flow and concentration values, so that a determination of compliance or noncompliance with categorical standards can be made.

- For significant industrial users subject to categorical standards, the report shall contain certification of compliance with those standards, signed by a certified professional.

13.19 	Reporting and Resampling of Discharge Limit Violations

- If, upon receipt of valid sampling and testing results, an industrial user becomes aware that a violation of discharge limits has occurred, the industrial user shall, within 24 hours of becoming aware of the violation, notify the Authority of this fact. Also, except as otherwise approved by the Authority and provided by 40 CFR §403.12 (g)(2)(i) and (ii), the industrial user shall also re-sample and analyze its discharge(s) for each parameter found to be in violation and report the result of the re-sampling and analysis to the Authority within thirty (30) days of becoming aware of the violation.

- Each significant industrial user shall have a duty, on receipt of validly obtained sampling and analysis results, of inspecting the results and determining if any wastewater discharge permit condition has been violated. Failure to examine and compare testing results with wastewater discharge permit conditions shall not be a valid defense for failure to comply with these reporting conditions.

13.20 	Sampling and Analysis

- Each industrial user shall perform waste stream sampling and analyses in accordance with its wastewater discharge permit or as otherwise required by the Authority.

- All sampling and analysis performed by the industrial user in compliance with wastewater discharge permit conditions, to prepare the reports required in subsections (16), (17), (18) and (19) of this Section, or as otherwise required by the Authority, shall be accomplished using techniques specified in 40 CFR, Part 136 or alternative procedures approved by the Authority and the Administrator. Unless otherwise required, all sampling should be performed during a normal production day and should reflect the usual and typical wastewater discharge of the user.

- The industrial user may monitor more frequently than otherwise required by the Authority. If the industrial user monitors any pollutant, subject to effluent limitations at the location designated for compliance monitoring, more frequently than otherwise required by the Authority, using the procedures set forth in 40 CFR, Part 136, or otherwise required, the results of such monitoring shall be included in the calculation and reporting of the data submitted to the Authority.

- Measurements, tests and analyses of the characteristics of wastewater shall be performed by a qualified laboratory which is certified by the Pennsylvania Department of Environmental Protection.  At the request of the Authority, qualifications shall be submitted for review.

- The industrial user shall ensure that all monitoring and analytical equipment it uses to monitor or otherwise analyze the pollutants discharged to the sewer system are periodically calibrated and maintained at intervals which ensure the accuracy of measurements.

- If sampling results indicate that the industrial user has exceeded an effluent limitation, the Authority, as an enforcement response to such violation, may require the industrial user to undertake increased sampling. Upon notification from the Authority, the industrial user shall undertake such additional monitoring as directed.

- Sampling schedules will be set by the Authority and the User may not be made aware of testing schedule.

13.21 	Monitoring Facilities

- The Authority may require an industrial user to provide and operate at the industrial user’s own expense, monitoring facilities to allow inspection, sampling and flow measurement of the wastewater or industrial waste discharge. The monitoring facility should normally be situated on the industrial user’s premises. The Authority may, when such a location would be impractical or cause undue hardship on the industrial user, allow the facility to be constructed in the public street or sidewalk area and located so that it will not be obstructed by landscaping or parked vehicles.

- There shall be ample room in or near such sampling manhole or facility to allow accurate sampling and preparation of samples for analysis. The facility, sampling and measuring equipment shall be maintained at all times in a safe and proper operating condition at the expense of the industrial user.

- Whether constructed on public or private property, the sampling and monitoring facilities shall be provided in accordance with the Authority’s requirements and all applicable local construction standards and specifications.

- Construction shall be completed within ninety (90) days following written notification by the Authority, unless the industrial user can show, to the Authority’s satisfaction, that a longer time period is necessary.

- The Authority, and its representatives, will have unrestricted access to the facility to inspect the sampling and monitoring equipment.

13.22 	Inspection

The Authority and its duly authorized representatives, including contractors, may inspect the facilities of any use to ascertain whether the purpose of the section is being met and all requirements are being complied with. Persons or occupants of the premises where wastewater is created or discharged shall allow the Authority or its representatives ready access at all reasonable times to all parts of the premises for the purposes of inspection, sampling, records examination and copying or in the performance of any of their duties. Areas which are subject to inspection include, but are not limited to, areas which could result in wastewater discharge to the sewer, such as manufacturing areas and chemical storage areas; pretreatment facilities; spill prevention and control facilities; hazardous waste generation areas; industrial self-monitoring facilities and areas where relevant documentation is kept or stored. The Authority and approval authority and their agents shall have the right to set up on the user’s property such devices as are necessary to conduct sampling, inspection, compliance monitoring and/or metering operations at the cost of the User. Where a user has security measures in force which would require proper identification and clearance before entry onto their premises, the user shall make necessary arrangements with its security guards so that, upon presentation of suitable identification, personnel from the Authority and approval authority will be permitted to enter, without delay, for the purpose of performing their specific responsibilities. It shall not be inferred, however, that the Authority is authorized to enter upon property of any industrial user under this subsection for any purpose in the event such entry is not otherwise allowable under Pennsylvania law.

13.23	Confidentiality

- Information and data on an industrial user obtained from reports, questionnaires, wastewater discharge permit applications, monitoring programs and from inspections shall be available to the public or any governmental agency without restriction unless the industrial user specifically requests at the time of submission and is able to demonstrate to the satisfaction of the Authority that the release of such information, processes or methods of production are entitled to protection as trade secrets of the industrial user. Wastewater constituents and characteristics shall not be recognized as confidential.

- When requested by the person furnishing a report and supported by evidence acceptable to the Authority as to need for protection as confidential material, the portion of a report which might disclose trade secrets or secret processes shall not be made available for inspection by the public but shall be made available to the Authority and, upon request, to governmental agencies for uses related to the this Section, the Authority’s NPDES permit, any State permit and/or industrial pretreatment program. In addition, such portions of a report shall be available for use by the State or any State agency in judicial review or enforcement proceedings involving the person furnishing the report.

- When information accepted by the Authority as confidential is transmitted to any government agency, a notification to the industrial user may be provided listing the confidential information transmitted and the governmental agency requesting it. The person seeking confidentiality protection of the information shall bear the burden of demonstrating to the governmental agency that such information is entitled to confidential protection.

13.24 	Records

- Users subject to the reporting requirements of these Rules and Regulations shall retain and make available for inspection and copying, all records of information and results obtained pursuant to any monitoring activities required by these Rules and Regulations.  Records shall include the date, exact place, method, time of sampling and the name of the person(s) taking the samples; the dates analyses were performed; who performed the analyses; the analytical techniques or methods used and the results of such analyses. These records shall remain available for a minimum of three (3) years. This period shall be automatically extended for the duration of any litigation concerning compliance with these rules and regulations, or where the industrial user has been notified of a longer retention period by the Authority.

- The industrial user shall furnish to the Authority, within a reasonable time, any information which the Authority may request to determine whether cause exists for modifying, reissuing, suspending or revoking a wastewater discharge permit or to determine industrial user compliance. The industrial user shall also furnish to the Authority, upon request, copies of records required to be kept. Where the industrial user becomes aware that it failed to submit any relevant fact in an application for a wastewater discharge permit, or submitted incorrect information in an application for a wastewater discharge permit, report to the Authority or in any other correspondence or communication pertaining to its industrial wastewater discharge, it shall promptly submit such facts or information.

13.25 	Certification Statements

- The following certification statement is required to be signed and submitted by Users submitting permit applications in accordance with Section 13.09; Users submitting baseline monitoring reports under section 13.16 and 40 CFR § 403.12 (l); Users submitting reports on compliance with the Categorical Pretreatment Standard under Section 13.17 and 40 CFR § 403.12 (d); and Users submitting periodic compliance reports required by Section 13.18 and 40 CFR § 403.12 (e) and (h). The following certification statement must be signed by an Authorized Representative as defined in Section 1:

I certify under penalty of law that this document and all attachments were prepared under my direction or supervision in accordance with a system designed to assure that qualified personnel properly gather and evaluate the information submitted. Based on my inquiry of the person or persons who manage the system, or those persons directly responsible for gathering the information, the information submitted is, to the best of my knowledge and belief, true, accurate, and complete. I am aware that there are significant penalties for submitting false information, including the possibility of fine and imprisonment for knowing violations.

SECTION 14   GENERAL PROVISIONS

14.01   If any section, paragraph, subsection, clause or provision of these Rules and Regulations is declared by a court of competent jurisdiction to be invalid, such decision shall not affect the validity of these Rules and Regulations as a whole or any other part hereof.

14.02   No agent, or employee of the Authority shall have the right or authority to bind the Authority by any promise, agreement or representation contrary to the letter of intent of these Rules and Regulations.

SECTION 15   BILLING

15.01   Failure to receive a bill shall not exempt the user from his responsibility to make prompt payment.  The presentation of a bill to the user is only a matter of accommodation.

15.02   Whenever ownership of a building is transferred, the new owner must file with the Authority an application for the continuation of the service as provided for in Section 20.01.  Failure to do so will result in the discontinuance of the sewer service.

15.03   The Owner of the real estate served by the sewer system shall be liable primarily, directly, and unconditionally for the payment of all charges and fees provided in these Rules and Regulations.*

*Section 15.03 was amended on December 12, 2022.

SECTION 16   LATE PAYMENTS

16.01  Charges for sewer rates and related charges shall be due upon receipt.  Payments received after the twentieth (20th) day of the month in which the payment is due shall be subject to a penalty (as set forth in the current Schedule of Fees and Charges) on the balance due.  Unpaid balances shall accrue simple interest per month (as set forth in the current Schedule of Fees and Charges) beginning on the thirtieth (30th) day of the month in which payment is due.  The Authority shall have the right to shut off and discontinue water service at the delinquent premises and not to restore service until all delinquent sewer bills and sewer charges and the cost of shutting off and restoring service shall have been paid.  All delinquent sewer rentals, charges and all penalties shall be subject to a lien against property in the Office of the Prothonotary of Bedford County and may be collected in a manner provided by law.**

16.02   Payments mailed as evidenced by the United States Postal Service on or prior to the end of the twenty (20) day period will be deemed to be a payment within time period.***

16.03	  A charge will be assessed to the customer any time where a check which has been presented to the Authority for payment on account has been returned by the payor bank for any reason.  The charge shall be double the amount billed to the Authority by the payor bank.****

** Section 16.01 was amended April 3, 1995, June 2, 2008, and December 12, 2022.

***Section 16.02 was amended August 3, 2009. ****Section 16.03 was added on December 12, 2022.

SECTION 17   DISCONTINUANCE OF SERVICE

17.01   Application for sewer service may be canceled or sewer service and/or water service disconnected on forty-eight (48) hours' notice for any of the following reasons:

A.  Failure of user to pay sewer bill and other charges when due.

B.  Tampering with any service pipe or permitting tampering by others.

C.  Use of sewer service by a user for any purpose other than described in the application.

D.  Use of sewer service by user at any location other than described in the application.

E.  Unlawful use of the sewer system by a user or discharge of prohibited wastes into the sewer system by a user.

F.  Permanent vacancy of building (more than 12 months).**

G.  Failure of user to maintain connection in good order.

H.  Refusal of access to property to authorized representatives of the Authority.

I.  Failure to comply with any sewer use restrictions which may be imposed.

J.  Violation by user of any of the Rules and Regulations.

K.  Pursuant to any other laws of the Commonwealth of Pennsylvania.

17.02   Any damage to  service line and/or sewer mains caused by careless undermining or by negligent excavating or backfilling of drains, sewers or other purpose shall be chargeable to the person causing damage, and if the charge to repair service line and/or sewer main is not paid within ten (10) days the Authority reserves the right to discontinue sewer service.

17.03   The Authority shall have the right to interrupt sewer service without notice in case of breakdowns or for other unavoidable causes, or for the purpose of making necessary repair or connections.  Reasonable notice will be given when practicable.

In no case shall the Authority be liable for any damage or inconvenience suffered.

17.04   When two (2) or more buildings are supplied through a single sewer service, any violation of the Rules and Regulations of the Authority by any one (1) owner shall be  deemed a violation by all, and the Authority may enforce compliance with this rule by shutting off the entire service, except that action shall not be taken until the non-violating owner(s) has/have been given a reasonable notice and opportunity to install separate connection.

** Section 17.01(F) was amended April 3, 1995.

17.05  Discontinuance of Service Due to Demolition of Building.

A.  Any person desiring to demolish, or otherwise permanently remove a building from a property served by municipal sewer or otherwise permanently disconnect a building from a property served by municipal sewer must apply to the Authority for permanent disconnection of service.

B.  Written notice of approval of the proposed disconnection will be made by the Authority to the applicant within seven (7) days following a regularly scheduled Authority meeting.

C.  For disconnection of sewer service, the property owner shall physically remove all service connection piping from the building served to the property line or edge of right of way if the Authority in its sole discretion deems it necessary.  The sewer lateral shall be capped or plugged to the Authority’s satisfaction.  The property owner shall restore the ground surface to its original condition following piping removal and closing of the corporation stop. All activities shall be witnessed by the Authority or their representative before being covered.  Contractors shall provide current liability insurance certificate prior to excavating.  This work that is deemed necessary by the Authority shall be completed at the Owner's expense.

D.  Reasonable and customary fees as set forth in the current Schedule of Fees and Charges may be charged by the Authority to cover Authority expenses incurred for application processing and disconnection inspection services.**

**Section 17.05 was added August 3, 2009 and amended on December 12, 2022.

SECTION 18   CHANGING RULES AND RATES

18.01   The Authority reserves the right to change or amend from time to time these Rules, Regulations,  and rates for sewer service, in a manner provided by law.

SECTION 19   SERVICE LINE AND SEWER EXTENSION EXPENSES

19.01   After initial sewer line implementation, construction of new sewer taps,  service lines and installation of pumps where necessary will be the financial responsibility of the individual applicant.   The service line shall be four (4) inches or more in diameter, depending on the review of the application   by the Authority and its engineer.

19.02   Where a sewer line is required to be extended to accommodate a new applicant, the cost of the sewer extension must be borne by the applicant.  Or the applicant may wait until the sewer line is   extended by community action and funding.

19.03   In either of the above cases, all service lines, connections, or sewer extension construction will be inspected and tested by the Authority.  Inspection and testing of a sewer extension will be at the expense of the applicant under the fee set forth in the current Schedule of Fees and Charges.  Materials used in construction or service lines or sewer extension must conform to or be equal to those defined in Sections 8.08, 8.09 and Section 9.*

*Section 19.03 was amended on December 12, 2022.

SECTION 20   MISCELLANEOUS CHARGES

20.01  The Authority shall not charge miscellaneous charges unless specified otherwise by the Authority in these Rules and Regulations.***

20.02.  Deleted on April 3, 1995.

20.03   Any owner desiring to transfer ownership of property and sewer service shall notify the Authority in writing of this desire and  a final bill will be prepared at no special charge to the owner.  The bill shall be due and payable within ten (10) days of transfer.

***Section 20.01 was amended August 3, 2009.

SECTION 21   CONNECTION CHARGE

21.01   Tap Fee (Before Sewage System Construction).  Upon making application for the issuance of a connection permit a tap fee of Five Hundred Thirty Dollars ($530.00), imposed by the Authority for collection by the Authority, will be charged for each building unit connected directly or indirectly to the sewer system.  If the owner or applicant pays this fee upon notification and before construction of the sewer system begins, said owner or applicant's tap fee shall only be Four Hundred Eighty Dollars ($480.00). Unless written permission is obtained from the Authority, a separate tap fee will be required for each individual occupied building, whether constructed as a detached unit or as one of a pair or row.

To be in accordance with Pennsylvania House Bill No. 444, any reference to connection fee in prior editions of these Rules and Regulations shall be deemed as the wastewater treatment plant construction portion of the tap fee.

The tap fee after April 6, 1992 shall be as set forth in the current Schedule of Fees and Charges per equivalent dwelling unit (EDU) unless provision for tap has been made by the applicant prior to this edition of the Rules and Regulations.*

* Section 20.01 was amended April 3, 1995, August 3, 2009, and December 12, 2022.

21.02   Deleted on August 2, 1993.

21.03   Tap and Capacity fees Along Existing Sewer Lines, Along New Sewer Extensions or in New Developments.  Any application for service received after December 31, 1996 for connection to an existing sewer main, a new sewer extension or in a new development will be subject to a sewer tap fee as set forth in the current Schedule of Fees and Charges, and a capacity fee per EDU as set forth in the current Schedule of Fees and Charges, even if a wye or a tee has been pre-set in said sewer main at that location.

A $1,600.00 capacity fee will be applicable to the Bedford Square Shopping Center subsequent to December 31, 1996.

The capacity fee (as set forth in the current Schedule of Fees and Charges) will also apply to development or subdivisions whereupon the building is determined to be a multiple use unit or a multiple dwelling unit.  In such case, the applicant is subject to a capacity fee of (“capacity fee” X "N") where N is the number of equivalent dwelling units (EDU) of the multiple user.

Any development building a sewer extension with the purpose of serving a proposed subdivision will be required to pay all construction and inspections costs in addition to the tap fee and the capacity fee per EDU as set forth in the current Schedule of Fees and Charges. **

** Section 21.03 was amended in its entirety on December 9, 1996.  Paragraphs 21.03 A and B were amended on August 2, 1993.  Section 21.03 was again amended on April 5, 2004 and on December 12, 2022.

SECTION 22   RATES

22.01  The sewer rates charged by the Authority for sewer service furnished by the sanitary sewer system shall be as follows:

Sewer rates per month per equivalent dwelling unit (EDU):

A-1 Commercial ....$ as set forth in the current Schedule of Fees

and Charges**

A-2 Residential....$ as set forth in the current Schedule of Fees and Charges**

A-3 Hospital   ....$ as set forth in the current Schedule of Fees and Charges

A. The rate for each EDU will be dependent on the Contract amount agreed to for construction of the sewage system.

B.  All commercial uses that discharge into the sanitary sewer shall be subject to a minimum charge of one (1) EDU, unless the EDU Rate Table below provides for a different EDU Rate.  The EDU Rate Table shall control.**

C.  The number of EDU's deemed to be served at each type of user shall be as follows:

Category                                  Equivalent Dwelling Units

a.  Each retail store, business,

industry or professional office:

1.  Ten (10) or less employees     		1

2.  Each additional five (5)       	½

employees over ten (10)

or fraction therefore

b.  Each business, industry, retail

store or professional office providing

showers for employees:

1.  Ten (10) or less employees   		1

2.  Each additional five				½

(5) employees over 10

(10) or fraction thereof**

c.  Each restaurant, club, tavern or

take-out eating establishment:

1.  Ten (10) or less employees			1

** Section 22.01 was amended on April 6, 1992, May 1, 1995 and then Section 22.01 was amended on July 1, 2006 and again on December 12, 2022.

** Section 22.01 B. was added on July 7, 1997.

**Section 22.01C.b was amended on August 3, 2009

2.  Each additional five (5) 			½

employees over ten (10) or

fraction thereof**

d.  Each business or professional office

attached to or part of the principal

dwelling of the businessman or professional

individual:

1.  With separate sanitary facilities		1

2.  Without separate sanitary facilities	½

e.  Each improved property having			1

a commercial (1 horsepower or

greater) garbage grinder, for such

grinder**

f.  Each hotel or motel (in addition to			½

restaurant facilities per rental room

g.  Each restaurant, club, tavern			1

or take-out eating establishment

per twenty (20) seats or fraction

thereof in addition to equivalent

dwelling units established for

employees as stated above**

h.  Each church						1

i.  Each private dwelling in which

apartments are let for a rental fee

in addition to the dwelling:

1.  With separate kitchen				1

and/or toilet facilities provided

j.   Each service station or

automobile repair garage:

1.  Three (3) bays or less				1

(without car wash facilities)

2.  Three (3) bays or less				2

(With car wash facilities)

3.  Each additional bay over three (3)***	½

**Sections 22.01C. c, e, g and j were amended August 3, 2009.

k.  Each school, per fifteen (15) pupils and		1

employees

l.  Each laundromat per five (5) washers or		1

major fraction thereof

m.  Each car washing establishment, per bay		2

n.  Each bowling alley (in addition to 			1

restaurant facilities or other facilities therein)

per six (6) lanes or major fraction thereof

o.  Each barber shop or beauty shop

whether or not attached to or part of

owner's residence:

1.  For the first two (2) chairs			1

2. For each additional chair**			1/4

p.  Each retail food market or store,

in addition to EDU's established for

employees:

1.  For meat and/or vegetable			1

preparation station

2.  For a bakery					1

3.  For a delicatessen				1

q.  Mobile home courts:

1.  Per mobile home (trailer)			1

space or lot

r.  Swimming pools:

1.  Per pool drain connected to

the sanitary sewer.

The charge for draining a pool to

the sanitary sewer shall be fifty

cents ($ .50) per thousand gallons

drained.  Authority to be notified

prior to opening of drain.

** Section 22.01.C .o  was amended on February 3, 1992 and amended on August 3, 2009.

s.  Camp grounds and motor home waste:

1.  For every three (3) campground		1

sites with waste hookup

2.  For each campground motor			1 ½

home dump site (including bus

restroom waste).

t.  Bedford County Memorial Hospital user

rate shall be broken down as follows:

1.  Operating and Maintenance Expense - These will be shared equally by all EDU's except that the Hospital will not be charged for any operating and maintenance costs associated with:

(a)  Grinder pumps

(b)  Septic tank pumping

(c)  Electric used to operate lift stations

2.  Debt Service - This will be shared equally by all EDU's except that the Hospital will not be charged for any debt service in connection with that portion of the development and construction costs associated with sewage collection lines.

22.01.C  Vacant Property Rate Adjustment - If a property is vacant with no furnishings for a period of at least sixty (60) days, the EDU monthly rate will be decreased to the debt service and reserve plus 10%.   The Owner of the property must provide the Authority with written notice by the twenty-fifth (25th) day of the third month after vacancy to receive the rate reduction.  The effective date of the rate reduction will start sixty (60) days after the property is vacated provided notice was given to the Authority.

Upon re-occupancy of the vacated property or unit, the Owner shall be obligated to notify the Authority so the regular sewer rate may again be charged.  The Authority reserves the right to inspect the property to determine whether it is vacant or not.**

22.02   Water Meter Installation - The Authority may require non-residential users to install at the user's expense water meters to monitor the user's use of water in order to determine the user's actual sewage use.  If the water meter readings indicate that the user's sewer use is greater than what it is being billed for pursuant to Section 22, then the Authority shall bill the user for its use based on actual use subject to the one (1) EDU minimum charge set forth in 22.01(C).  This provision shall apply to current and future users of the Authority.**

** Section 22.01.C was added October 2, 1995

** Section 22.02 was added April 4, 1994.

** Section 22.02 was changed on July 7, 1997.

22.03  Water Meter Rules**

A.  Installation  - The Owner of the non-residential property will provide, free of charge and expense to the Authority, a location for installation of a water meter in areas where public water service is available.  Generally, this location is to be a readily accessible spot inside the Building near the entrance of the Service Line.  The Owner will also provide an exterior location for the remote readout portion of the water meter.

The Authority's inspector shall signify his approval of the water meter connection by endorsing his name and the date of approval on the meter information sheet turned into the Authority.

The Authority by its duly authorized representatives and employees, bearing proper credentials and identification, shall be permitted to enter upon the Owners' property for the purpose of inspection, observation, testing and retesting of the water meter and connection; at all reasonable hours.

A separate water meter will be required for each building, whether constructed as a detached unit or as one of a pair or in a row.  A single connection will be permitted to serve a school, factory, other permanent multiple dwelling unit or multiple use unit structure whose individual units may not be subject to separate ownership.  A single connection will be permitted for a mobile home park, as long as each mobile home is individually metered.

The Authority reserves the sole right to remove a water meter from its setting.  Should it be necessary to remove a water meter from its setting, notice shall immediately be given to the Authority.***

B.  Water Meter Maintenance - All water meters are the property of the Authority and will be maintained and repaired by the Authority.  The Authority will assume the cost associated with ordinary wear and tear.  However, should damage to the water meter occur due to freezing, hot water, carelessness or negligence by the Owner, the repairs shall be at the expense of the Owner.

The Owner shall notify the Authority of any damage to or any cessation in registration of the water meter, as it comes to his/her knowledge or the knowledge of any user of his/her Connection.

No seal placed in the water meter by the Authority shall be tampered with or defaced.  It shall not be broken except upon authorization from the Authority.  Where the seal is broken, the Authority reserves the right to remove the Meter for test at the expense of the Owner.  It is a violation of Clause 6, Section 34, Act of 1974 of the Laws of Pennsylvania to break or deface the seal of, or otherwise damage the water meter.

A bill for repairs or replacement of a damaged water meter will be submitted to the Owner and shall be due within thirty (30) days after the billing date.

C.   Water Meter Reading and Billing - All water meters shall be read monthly, by the Authority, insofar as possible.  The quantities recorded by the water meter shall be considered conclusive on both the Owner and the Authority, except when the water meter has been found to register incorrectly or has ceased to register.

In this event, the Authority will estimate the bill; taking into consideration average past registrations, or by another fair or reasonable method.  The finding thus determined shall be final and binding upon both parties.

In any instance where a building has not had a water meter installed, the Authority will estimate the bill; taking into consideration usage by other buildings having similar characteristics, or by another fair or reasonable method.  The finding of the Authority in this regard shall be conclusive upon both parties.  However, if the absence of a water meter is a result of refusal or failure of the Owner of the building to have a water meter installed, the bill for service during such period shall be established by the Authority at an amount equal to the maximum bill for any building of similar characteristics.  The determination of the Authority in this regard shall be conclusive upon both parties.

** Section 22.03 was added September 11, l995.

***Section 22.03A was amended on August 3, 2009.

D.  Water Meter Testing - If requested in writing by Owner, the Authority will conduct a test of the accuracy the Meter supplying his Building.  A deposit of one hundred dollars ($100.00) shall accompany the request.  The Authority shall record the actual labor and other expense involved.  A minimum of two hours labor will be charged.  If the Meter is found to be registering more than AWWA specifications allow, the Owner will not be billed, and his deposit will be returned.  If the Meter is within standards, the Owner will be billed for testing.  The unused portion of the deposit will be refunded.

SECTION 23 CHANGES IN CLASSIFICATIONS

23.01   If use or classification of any property should change within any quarterly period the difference in the sewer rental, pro-rated on a per diem basis will be charged or credited, as the case may be, on the bill for the succeeding quarterly period.  Additional classifications and additional sewer rentals may be established by the Authority from time to time.

SECTION 24   TIME AND METHOD OF PAYMENT

24.01   Sewer rentals or charges shall, unless otherwise provided herein, shall be paid monthly with due dates being the 20th of the following month.  If the 20th is a Sunday, the 21st shall be the due date.

SECTION 25   PENALTIES

25.01  In addition to complying with the provisions of Section 16.01 with respect to the payment of sewer rates and charges, all property owners connected to the sewer system must give the Authority their correct address. Failure to receive bills will not be considered an excuse for non-payment nor permit an extension of the period during which bills are payable at face.***

A.  With respect to tenants, the landlord will be notified of any delinquent account after 30 days.  After 60 days, the owner will be responsible for payment of all costs.  Service may be discontinued at this time, and/or legal action shall be taken.***

25.02  The Township of Snake Spring shall adopt by ordinance the enforcement provisions of these rules and regulations and, accordingly,  will  exercise their police power  to enforce these rules.  Any person failing to make a proper connection to the sewer system within the time specified after receipt of proper notice or after obtaining a time extension or any person providing false or incorrect information to the Authority or any person failing to comply with the usage requirements shall upon conviction thereof before a District Justice, pay a fine or penalty of Fifty Dollars ($50.00) for each day in violation.**

25.03   All persons violating any portion of the Rules and regulations will be in violation of these rules.  Notice of such violation shall be sent through the United States mails and if, after thirty (30) days of elapsed time no action on the violation is taken, the sewer connection shall be removed or closed and reconnection will not be made until after a correction of the violation has been made.   The expense of such removal or closing and the expense of restoring the sewer service shall be a debt due the Authority and a lien upon all the property of the user, and may be recovered by civil action in the name of the Authority or the Township.

25.04   In addition to any penalty hereinabove prescribed, any person violating any of the provisions of these rules and regulations shall, upon conviction thereof before a District Justice be fined consistent with Snake Spring Township’s Sewer Hook-Up Ordinance and/or in default of payment thereof, be sentenced to undergo an imprisonment pursuant to Snake Spring Township’s Sewer Hook-Up Ordinance.**

*** Section 25.01 and 25.01A were amended August 3, 2009.  Section 25.01B was deleted August 3, 2009.

** Section 25.02 was amended on July 11, 1994.

** Section 25.02 was amended on July 11, l994.

**Section 25.04 was amended on August 3, 2009.

SECTION 26   REGULATIONS BY AUTHORITY

26.01   The Authority Board of Directors may  make and enforce such rules and regulations for the safe, economical and  efficient management, control and protection of the public sanitary sewer system, and for the regulation, collection, rebating and refunding service charges as may be needful or necessary from time to time.

26.02   Compliance:  The Authority shall be authorized to assure compliance with these Rules and Regulations to inspect, upon reasonable notice to a User, the User's premises.  The Authority shall be authorized to request payroll record information concerning who is employed by a User to determine the number of Employees.  This does not authorize obtaining any payroll information.**

** Section 26.02 was added on July 11, l994.

SECTION 27   REPEALS

27.01   All resolutions, rules, or regulations or parts of resolutions, rules or regulations not in accord with these rules and regulations are hereby repealed insofar as they affect these rules and regulations.

27.02   Invalidity of any section, clause, sentence or provision in these rules and regulations shall not affect the validity of any other section, clause, sentence or provision which can be given effect without such invalid part or parts.

27.03   The Authority through its duly qualified officers, reserves the right to amend these rules and regulations in part or in whole accordance with law whenever it may deem necessary.

SECTION 28   INITIAL EFFECTIVE DATE

28.01   These rules and regulations shall take effect on the 10th day of  September, 1990 and all rates hereinabove provided for as sewer service charge shall become and be effective thereafter upon bills rendered from and after the 10th day of September, 1990.

ADOPTED as amended by the Board of Directors of the Snake Spring Township Municipal Authority in lawful session assembled this ____ day of December, 2022.

SNAKE SPRING TOWNSHIP

MUNICIPAL AUTHORITY

By________________________________

Chairperson

__________________________________

Secretary

ATTEST:

______________________________